## 2020
Date | Description of Event | Pollutant | Exceedance Type | Best estimate of the quantity or the rate of emission | Measures taken, or intended to be taken, to prevent a recurrence of the incident.
2020-09-07 | Boiler 2 had an intermittent instrument communication fault which was creating difficulty in combustion control, this resulted in frequent spikes in the emissions at the South release point. This combined with sub optimal Lime dosing particularly on FGT stream 2, created HCL spikes which although not concerning for 30min limits did accumulate to tip the daily average over the limit. Lime reagent dosing was increased and Boiler 2 firing parameters were adjusted in order to minimise emissions. | HCl | Daily Average | 10.6 mg/Nm3 | Replacement of the lime dosing screws is planned to be completed next year. HCl and SO2 instrumentation, downstream of FGT, have been sent to Germany for calibration.
2020-09-08 | The quench bath was blocked due to poor combustion of wet waste from the bottom of bunker 4. The blockage caused material to build up in front of the Start Up Burner. This disrupted the normal formation of the flame and thus stopping the correct mix of gas and air causing emission challenges. | CO and TOC | CO (Daily Average) TOC (3x30 minute exceedance) | CO = 52.97 mg/Nm3 (Daily average) | Improve the drainage in bunker 4 to ensure the waste is less wet at the bottom of the bunker. Project proposal is in place to do bunker crane automatisation which in turn will improve waste mixing.
2020-10-17 | During the delivery of hydrochloric acid, it appears that some HCl was vented into the air. | HCl | Fugitive | N/A | The delivery driver, admitted that there was a small release of vapour whilst venting off. The delivery company believes the driver has deviated from his training, specifically the correct procedure for discharging a road tanker, relating to the process of venting off HCL fumes, and has also failed to report this to his Company. The root cause of this incident was an operator error. The driver was suspended by the contractor from the ICL contract until he has been fully assessed by an ICL Driver Trainer.
2020-10-31 | Unexplained spike of dust experienced on the south stack. This momentary spike led to an exceedance of the 30 min average. No abnormal running conditions were experienced during, before or after this event, suggesting that this was a momentary blip of the analyser/instrumentation. The South Standby analyser did not pick up any abnormality, indicating that this might have been caused by an instrument error. | Dust | Short Term (30-minutes) | 52.4 mg/Nm³ | Analyser specialist investigated both duty and stand-by analyser, and found no fault with any of the analyers. Nature of the spike indicates that some debris may have dislodged from the internal side of the stack and affected the duty dust analyser. The operation team confirmed that the plant was in full operation with no mechanical or electrical issues.

## 2021
Date | Description of Event | Pollutant | Exceedance Type | Best estimate of the quantity or the rate of emission | Measures taken, or intended to be taken, to prevent a recurrence of the incident.
2021-03-20 | Simultaneous blockage on FGT 1/FGT 2 Lime and PAC injection venturi’s. Blockages cleared by Operations. Emission levels returned to normal parameters. Operational checks on Venturi’s have also been increased. | HCl | Short Term (30-minute) | 61.3 & 60.8 mg/Nm3 | Increased operational checks on lime/PAC injection venturi systems.
2021-06-09 | There was a release of APC on FGT 1 in the amount of approximately 500kg. A denseveyor vent valve blew off causing residue emission to the atmosphere, covering adjacent plant and areas below with residue. All affected areas were taped off to prevent unauthorized access and disturbance of the material. Area was cleaned up by the Maintenance Department immediately. | APCr | Fugitive (Spillage) | 500 Kg | Preventative maintenance to be set up for the vent tube. In addition to this, modification of the display screen to be consistent with the field operations.
2021-06-15 | Samples of surface and sewer water for quarterly Q2 reporting to EA both exceeded permit level of 20 mg/m3 for oil and grease. | Oil / Grease | Quarterly Sampling | 33.2 mg/l & 37.6 mg/l | Subsequent surface sewer water sampling for Q3 came back as below detection limits. Samples taken in September, October and November all had oil and grease levels below detection on the sewer sampling point. It is concluded that high level of oil in surface and sewer water detected in June 2021 was intermittent and of unknown origin.
2021-06-28 | Sudden explosion of gas bottles was a sole cause of this exceedance. | TOC | Short Term (30-minute) | 25.5 mg/Nm3 | Improved management of waste inspections to reduce the risk of pressurised gas bottles being unloaded into the bunkers and fed into the boiler feed hoppers.
2021-06-29 | CO daily average on South Stack was exceeded due to Boiler 1 Rollergrate overheating. Gas burners were put into service immediately. Further operational procedures were also immediately instigated to minimise the production of CO. | CO | Daily Average | 61.93 mg/Nm3 | Inspection of all bunker house drainage system, planned in 2022 will resolve problem with the wet waste at the bottom of the bunker.
2021-06-29 | 1 x 30-minute TOC experienced due to Boiler 1 Rollergrate No:1 overheating resulting in temporary loss of operation. Air flow increased to Rollergrate No:1 to aid cooling before returning to service. | TOC | Short Term (30-minute) | 30.2 mg/Nm3
2021-07-03 | 30 Minute TOC Exceedance experienced due to poor combustion and Boiler 4 Holding Burner tripped twice due to a flame eye issue. Attempted to maintain furnace temperatures with Start-Up Burner only, but not successful. | TOC | Short Term (30-minute) | 41.6 mg/Nm3 | Increase inspection on flame eyes in order to prevent occurrence of future failures.
2021-07-19 | Sudden explosion of gas bottles was a sole cause of this exceedance. | TOC | Short Term (30-minute) | 49.9 mg/Nm3 | Improved management of waste inspections to reduce the risk of pressurized gas bottles being unloaded into the bunkers and fed into the boiler feed hoppers.
2021-09-07 | 2 x 30 mins dust exceedances experienced due to damaged baghouse filters in FGT 3 Compartment No:2. FGT 3 Compartment 2 isolated. | Dust | Short Term (30-minute) | 54.5 mg/Nm3 & 32.6 mg/Nm3 | Damaged filters were replaced before returning to service.
2021-09-23 | Fire started at the BWRF within a pile of mattresses that were waiting to be collected from the slab. Several operatives attended the fire.The London Fire Brigade were called who arrived on site just after 15:00. The flames were extinguished and the LFB left site approx. 17:00. | Smoke | N/A | N/A | Further measures to be implemented: Waste Operations team to review the storage of mattresses in terms of separation distances and storage times and record findings confirming if any further control measures are required. Training to be arranged for all FPP staff on how to use large fire extinguishers.
2021-10-18 | Root Cause Analysis (RCA) into the first turbine trip – TA2 – found no evidence to suggest an external influence from the grid or from any other parts of the plant. That leads LEL to conclude that the most probable cause of the trip was fatigue of an aged plant and equipment. RCA regarding the second of tripping TA1 and the loss of voltage on EEBT1, LEL concluded that the most likely cause being that with VT fuses rapturing on TA2 and being coupled with TA1 and EEBT1 when attempting to synchronise, caused further VT fuses to rapture, preventing synchronising. | CO | 95th %ile Exceedance | Multiple across both stacks. | Recommendations from the investigations and RCA are as follows: LEL replace all High Voltage 11kV switchgear and their associated equipment with modern equivalents, this will include replacing the existing electromechanical protection relays with modern multifunctional electronic protection relays. This can likely be put under abnormal conditions.
2021-11-02 | During the delivery of lime there has been an uncontrolled release of 2 tonnes of lime from the lime silo on FGT 3. | Lime | Fugitive (Spillage) | 2000 Kg | The procedure for the delivery of the lime has been changed to incorporate reduction of pressure when the weight of silo reaches 28 tonnes. An engineering project has also been initiated to automatically reduce the delivery pressure when the weight of the lime silo reaches a certain limit.
2021-12-24 | A sudden explosion of gas bottles was a sole cause of this exceedance. | TOC | Short Term (30-minute) | 40.7 mg/Nm3 | Improved management of waste inspections to reduce the risk of pressurised gas bottles and other non-conforming waste being unloaded into the bunkers and fed into the boiler feed hoppers.
2021-12-25 | 1 x 30 minute dust excursion, due to two flue gas treatment streams suffering ruptured filter bags simultaneously (FGT 3 & 4). 2 x compartments (1 from each stream) had to be identified from a possible 8 compartments in order to identify the source and then be shut off to prevent any further release of dust. The filter bags will be replaced before opening the compartments back onto the gas streams. | Dust | Short Term (30-minute) | 44.2 mg/Nm3 | Damaged filters were replaced before being returned to service.

## 2022
Date | Description of Event | Pollutant | Exceedance Type | Best estimate of the quantity or the rate of emission | Measures taken, or intended to be taken, to prevent a recurrence of the incident.
2022-01-07 | Contractors were clearing blockages in the Flue Gas Treatment (FGT) hoppers. Between 12:00 and 12:30, there was an uncontrolled release of 2 tonnes of Air Pollution Control residue (APCr) from FGT 3 hopper to the ground. | APCr | Fugitive | 2000 Kg | Contractor working procedures are to be reviewed and updated as necessary.
09/02/2022 | Dust exceedance, due to flue gas treatment stream 2 Preheat dampers remaining open with the main stream in operation following a period of preheating before start up. This caused a bypassing of the filter baghouse. | Dust | Short Term (30-minute) | 31.9 & 48.4 mg/Nm3 | A review of the dampener logic control was carried out by operations in conjunction with the relevant contractor to ensure the control was suitable for the operation. Following review, the logic was deemed suitable for the abatement system.
10/02/2022 24/04/2022 07/05/2022 02/06/2022 10/06/2022 18/06/2022 29/06/2022 13/07/2022 16/07/2022 29/07/2022 08/08/2022 11/08/2022 10/09/2022 11/11/2022 17/11/2022 21/12/2022 | Explosion in the boiler, which the cause is anticipated to be gas bottles within the municipal waste stream. | TOC | Short Term (30-minute) | multiple Short-Term TOC exceedances due to gas bottle explosions. | On-going review on measures that can be done to prevent waste (Gas bottles) entering the municipal waste stream.
28/02/2022 01/05/2022 | Ruptured filter bags on Flue Gas Treatment Stream 2 caused elevated levels of dust throughout the day leading to the exceedance of the daily average limit | Dust | Daily Average | 10.97 mg/Nm3 | Damaged filters were replaced before being returned to service. The condition of filter bags for all lines will be assessed during Bag Filters outages.
2022-03-31 | Release of 2,000 kg of lime from the lime silo on FGT 3 and 4. This took place during the delivery of lime. | Lime | (-) | 2000 kg | Several engineering measures have been modified and checked in assosiation with the lime silo.
02/05/2022 03/05/2022 | Due to the events on 29th April (loss of power to the site – 11kV Switchgear replacement), waste was held in the bunkers for a longer period thanduring normal operation, this caused issues with stabilising the combustion of waste due to the change of quality and composition of waste. | CO | Daily Average and 95th %ile | 60.68 mg/Nm3 (Daily Average) | New 11kV Switchgear was successfully commissioned and the fault on the system, which caused power distortion resolved.
2022-06-07 | A trial pit was excavated adjacent to East Road. Excavated material was removed and a black hydrocarbon-like liquid was identified in the bottom of the trial pit. The trial pit will be extended to identify the extent and a possible source for the substance | Potential Contamination | N/A | N/A | A sample for analysis was taken. The sample was sent to an external company to identify a full specification ofresults. The conclusion from the sample results indicated no remediation or special attention was required for contamination reasons.
2022-08-24 | Boiler 1 seized roller grate 1 and fault with one of the gas burners. Waste feed was ceased, a start-up burner was put in service and other adjustments were made to try to control emissions and stabilise the boiler. | CO | Daily Average and 95th %ile | 52.8 mg/Nm3 (Daily Average) | Roller grate and gas burner servicing and maintenance. Further control on temperatures and damper will be put in place
2022-09-02 | Due to a Turbine trip at 16:38hrs, boiler loads were rapidly reduced to lower steam range pressure and these rapid load adjustments coincided with working the bottom of Bunker 4 which contained wet shredded waste. Combustion became unstable during this period. | CO | 95th %ile | 151.7 mg/Nm3 | Changes have been made to the waste movement process to ensure that the bulky waste tipped into outside bays by borough vehicles is transferred into the TBWRF building at the end of the diver shifts.
2022-09-14 | Damaged baghouse filters in FGT 4 compartment 1. | Dust | Short Term (30-minute) | 85.7 mg/Nm3 | Following isolation and identification of the damaged bag filter, the damaged filters bags were replaced.All bag filters across the bag house compartments are to be changed during the future FGT outage.
2022-10-17 | FGT 3 Denseveyor vessel over pressurised causing a failure of the vent sock which in turn released some APCR into the surrounding area | APCr | Fugitive | 50 Kg | Tthe DCS and control logic associated with the system, modifications have been implemented to inhibit the manual reset button when there is high pressure active within the system.
2022-10-12 | Notification of Automated door failures at the facility. Having the doors open results in greater chance of odour escape from the facility. There is also greater chance of litter escape from the bays to the surrounding area. | Odour and Litter | (-) | (-) | Program of works to ensure doors are made operational or permanently closed for the remainder of the facility life. nspection frequency and facility images are to be recorded by the operations department on a more recurrent basis to ensure housekeeping standards on site are maintained.

## 2023
Date | Description of Event |  | Reason | Measures taken to prevent reoccurrence
2023-01-10 | YP3033BE_EP_2023_AE001 | 1 x 30 minute TOC exceedance was observed between 13:59 – 14:29 pm. During this period, boiler 1 experienced an explosion from a suspected gas bottle causing CO and TOC to momentarily spike to very high levels which subsequently cleared. | Gas bottle explosion | Adjustments were made to try to control emissions and to stabilise the boiler, which reduced the emissions following the explosion. | Information taken directly from EAs annual performance report template for 2023. The EAs annual performance report was modified in 2023 for operators to include information assosiated with permit exceedances. Information provided in the annual performance report assosiated with exceedances are displayed.
2023-02-17 | YP3033BE_EP_2023_AE002 | The mechanical team were attempting to clear a blockage on the precipitator on boiler 4. An access door was opened in order to remove the blockage to allow the material to move freely. The blockage was cleared, however the material that had built up on top of it started releasing through the opened door. The material built up on the floor under the precipitator and the area was cordoned off and immediately cleared up. | Lime screw blockage | Not identified, the door design was different to that typically for the other precipitators - Did not have hinges on the door design. This prevented the door to be opened gradually in a controlled manner. Modifications were made to the door and additional signage has been placed to prevent re-occurance.
2023-03-06 | YP3033BE_EP_2023_AE003 | 6 x 10 minute CO Exceedances contributed towards the 1 x daily Average CO exceedance. Several explosions from Boiler 1 in a short period of time was noted between 20:00 – 20:30hrs, which caused the daily average to go over 50 mg/Nm3. The waste from bunker 2 was seen to be wet, which contributed to poor performance. Emissions of CO decreased, but the daily average recorded 51.14 mg/Nm3 for the day. | Gas bottle explosion | CO Estimation tool has been developed to anticipate boiler explosion impacts on the emissions to allow a more proactive monitoring method.
2023-03-07 | YP3033BE_EP_2023_AE004 | 9 x 10 minute CO Exceedances observed by several explosions throughout the day. Significant spikes were observed between 19:00 – 20:00 pm within Boiler 3, which affected both A1 and A2 stack emissions. Poor refuse material from Bunker 5 is the expected cause of increased emissions. It was instructed to stop feeding from bunker 5. Further plant adjustments were made and holding burners were put in service to control emissions and stabilise the boiler. | Waste quality
2023-03-07 | YP3033BE_EP_2023_AE005 | 7 x 10 minute CO Exceedances contributing towards the 1 x daily CO exceedance. Significant spikes were observed between 19:00 – 20:00 pm within Boiler 3, which affected both A1 and A2 stack emissions. Poor refuse material from Bunker 5 is the expected cause of increased emissions. It was instructed to stop feeding from bunker 5. Further plant adjustments were made and holding burners were put in service to control emissions and stabilise the boiler. | Waste quality
2023-03-13 | YP3033BE_EP_2023_AE006 | 30 Minute TOC Exceedance experienced due large gas bottle explosion within Boiler 4, resulting in poor combustion. Adjustments made to maintain stable combustion, but was not able to recover to within our limits in the specified time period. | Gas bottle explosion | As illustrated in the Part A, the operation team witnessed an explosion within one of the boilers. As all other process parameters remained in steady state, it is anticipated that the cause was a gas bottle entering the system
2023-03-17 | YP3033BE_EP_2023_AE007 | When bringing boiler 4 offline (Conducting shut down procedure), the gas burner tripped at the late stage of shut down, bringing the temperature below 8500C. This caused an increase in TOC being observed on the North stack, which resulted in a half hourly ELV breach between 23:29hrs to 23:59hrs. Waste was not being fed at the time of the exceedance, but there was residual waste on the grate. | Burner Trip | In effort to improve gas burner reliability in operation, LEL has called a specialist service contractor to: • Report on the current state of gas burner and what is needed to improve and recommendation for parts to be replaced • Annual Supporting visit for gas burners servicing First visit had taken place on 04/07/2022
2023-04-05 | YP3033BE_EP_2023_AE008 | 1 x 30 minute TOC exceedance: Boiler 2 Feeder Ram stopped operating for a period of time due to a mechanical fault. Whilst recovering the Feeder Ram operation, the Holding Burner tripped, resulting in loss of furnace temperature, which resulted in an increase in emissions. Adjustments were made to try to control emissions and to stabilise the boiler, but we were unable to recover within the specified period. | Burner Trip
2023-04-17 | YP3033BE_EP_2023_AE009 | 1 x 30 minute TOC exceedance – Boiler 2 Drum level was lost during a period of poor quality wet waste from the bottom of bunker 2, forcing the boiler into emergency shut down, resulting in a loss of both gas burners, primary and secondary air fans causing a drop in furnace temperature. Adjustments were made to stabilise the boiler, but we were unable to recover within the specified period. | Burner Trip
2023-05-07 | YP3033BE_EP_2023_AE010 | 1 x 30 minute TOC exceedance – Boiler 5 feeder ram failed due to a false signal, resulting in a gap in the furnace. The holding burner failed to ignite at the same time. Adjustments were made to both the primary and secondary air fans along with use of the startup burner to stabilise the combustion chamber, but we were unable to recover within the specified period. The Holding burner and feeder ram front limit switch have now been repaired & proved to work when required. | Burner Trip
2023-05-26 | YP3033BE_EP_2023_AE011 | Challenging waste entered the boilers between 10:59am – 11:29am, creating large spike in SO₂ and elevated levels of HCL. The operations team increased lime dosing across Flue Gas Treatment (FGT) Streams 1 & 2 to mitigate raised acidic emissions, however, the team encountered partially blocked lime screws on both streams. The operations team attended the FGT streams and carried out a manual flight aeration and screw unblocking procedure, which increased lime dosing immediately, but there was insufficient time within the 30 minute period to recover from the excessively high SO₂ readings. Emission levels reduced following this and remained low for the remainder of the day. | Waste quality | Following a review with both the operations team and mechanical department, the following corrective measure is to be placed to prevent re-occurrence. • The frequency of the plant preventative maintenance conducted on the aerators by the mechanical department will be inputted into the system for a weekly check.
2023-05-27 | YP3033BE_EP_2023_AE012 | Between the period of 13:29hrs to 13:59hrs, challenges were faced with the gas burners (Holding and start-up) on boiler 3, which cause unstable combustion. This resulted in an increase in TOC and CO, which resulted in a 30 minute TOC exceedance of 24 mg/Nm3 in comparison to the emission limit value of 20 mg/Nm3. Combustion conditions stabilised and remained low for the remainder of the day. | Burner Trip | In effort to improve gas burner reliability in operation, LEL has called a specialist service contractor to: • Report on the current state of gas burner and what is needed to improve and recommendation for parts to be replaced • Annual Supporting visit for gas burners servicing First visit had taken place on 04/07/2025
2023-06-04 | YP3033BE_EP_2023_AE013 | 1 x 30 minute TOC exceedance – Due to feeder ram failure combined with gas burners (holding & start-up) failing on boiler 4. Temporary repair carried out. Spares parts required are on order. | Waste quality | Following investigation, the following actions will be implemented to target waste quality at the bottom of the bunker: - Operations to add health check of the sump pumps to the daily operational checks - Operations to roll out bunker management instructions to crane drivers.
- | YP3033BE_EP_2023_AE014 | ’There is no exceedance relating to AE014 and this reference number was not used for the 2023 exceedance list | - | -
2023-07-05 | YP3033BE_EP_2023_AE015 | HCl daily limit exceedance due to challenges with the FGT1 Lime silo discharge screw. As FGT2 is on it’s planned outage, during this period the south stack was only being fed by the FGT1. Boilers 1 & 2 loads were reduced to mitigate emissions. Maintenance department were promptly notified of FGT1 lime silo discharge screw jammed and made efforts to rectify. The MMD successfully un-blocked the line and further support was required by the E&I department to re-instate the operation of the screw. | Lime screw blockage | Following an investigation involving the mechanical and operations department the following actions will be performed to mitigate any re-occurrences: - Run Solenoid Failure report on D365 in 6 months time on Lime system (FGT) to review frequency of failure. - Investigate interlock system on Lime Screw feeder(s) system to prevent screw feeding operation when pneumatic valve at exit is closed. Validate effectiveness of logic.
2023-07-23 | YP3033BE_EP_2023_AE016 | TOC 30 minute limit exceedance – Due to a large explosion from suspected gas bottle in boiler 5. Spike was so high the average could not be reduced sufficiently even with a level of 1.1mg for the remaining 25 minutes | Gas bottle explosion | The site has recently started recording the gas bottles explosions more granular.
2023-07-28 | YP3033BE_EP_2023_AE017 | Late in the evening, one of the sump pumps in the boiler basement tripped. Instead of tripping the local protection, the trip occurred at the main distribution board. This resulted in power issues to both boiler 1 and boiler 5, placing both into emergency shutdown. | sump pump failure | Following an investigation involving the E&I and operations department, the following corrective actions were collated: - Design protection is 100 amp fuse. Reduce fuses in sump pump starter within C10 to 63 amp. - Investigate the potential of using C6 as primary instead of C10. This will need coordination with operations on availability for investigation in line with plant availability. - Install smaller capacity fuses to protect 400-amp circuit breaker - Investigate UPS functionality for Boiler 1, 4 & 5 to confirm operating as expected - Create a robust OTNOC plan.
2023-07-28 | YP3033BE_EP_2023_AE018 | Late in the evening, one of the sump pumps in the boiler basement tripped. Instead of tripping the local protection, the trip occurred at the main distribution board. This resulted in power issues to both boiler 1 and boiler 5, placing both into emergency shutdown. Operations also manually conducted an emergency shutdown of boiler 4 due to an increase in water flow to the boiler following the shutdown of both boiler 1 & 5. Power was restored to the board and the plant was brought back online in a controlled manner. | sump pump failure
2023-08-04 | YP3033BE_EP_2023_AE019 | The operations control room lost CEMs communication at 08:15 am. Following further investigation, the connection between the SICK panels and Envirosoft PC (Data Acquisition Handling System (DAHS)) had been lost. IT was requested to attend site out of hours and data returned to the DAHS by 12:30 pm. Information within the CEMs analyser cabinet was still available during the period, but data to the DAHS was not registering and not available during this period. | Data loss | Following an internal review and discussion with IT, who rectified the issue at the time, the following actions are to be progressed: - Investigate power supply and remediate if required within the CEMS cabinet. - A lesson learnt / Event log is to be circulated to raise awareness of remediation in a similar instance of data loss. - Additional support with the DAHS has been requested from our CEMS system support contractor, which suggested to replace the DSU, which will be pursued by LEL.
2023-08-20 | YP3033BE_EP_2023_AE020 | 1 x 30 minute Dust Exceedance whilst attempting to carry out a precoat procedure on FGT Stream No.4 after maintenance. The Main Inlet damper was shut at time of the emission, but as soon as lime was introduced for the precoat, the dust reading increased. Suspect filter bag issue within a compartment. Actions were carried out to reduce dust levels, by shutting down precoat procedure, ceased lime dosing and closing the FGT Stream Main Outlet Damper, but we were unable to recover within the specified 30min period | inadequate procedures | • Create Handover procedures or add a section on D365 for works handover (Written and recorded) • A final checklist for MMD handover to be developed
2023-08-21 | YP3033BE_EP_2023_AE021 | 1 x 30 minute TOC exceedance – Boiler 2 Holding Burner ignition and stability issues. Whilst attempting to raise steam on Boiler 2, the holding burner tripped and failed to re-ignite. Root cause found to be damaged cables on a Flame Eye. Flame eye was replaced with alternative and holding burner ignited and burner flame was stable. TOC levels during the period were elevated and reduced once stable flame established. We were however unable to recover to permitted levels within the specified time frame. | Burner Trip | Flame eye was replaced with alternative and further maintenance review conducted.
2023-05-21 | YP3033BE_EP_2023_AE022 | Following investigation into a discrepancy identified between the NOx values from the south Duty and standby analysers it was identified that an error in the development of the QAL2 function for the south standby analyser was identified during the previous campaign performed by the periodic monitoring company. Data was evaluated eliminating the south standby readings to identify if there were any exceedances with the more accurate analyser. | Function Error | Following further review, the following points have or are to be performed to rectify any information. • Part A reports have been sent to the EA and corrections are to be made to the WID reports sent to discard the error data. • Alterations have been made to the QAL2 contract to ensure 3 yearly QAL2 is performed on the analysers AST / QAL2 tracker has been developed providing visibility on previous and up-coming testing requirements
2023-07-15 | YP3033BE_EP_2023_AE023
2023-07-16 | YP3033BE_EP_2023_AE024
2023-07-17 | YP3033BE_EP_2023_AE025
2023-07-16 | YP3033BE_EP_2023_AE026
2023-09-08 | YP3033BE_EP_2023_AE027 | 1 x 30 minute TOC exceedance – Boiler 5 had an explosion due to suspected gas cylinder within waste stream. TOC lemissions spiked, O2 reduced to 6.2% and CO emissions spiked along with furnace temperature spiking to 1000deg c. We were however able to quickly control the firing of the boiler and brought the furnace to a normal operating condition within a few minutes but the TOC spike took us just over the 30 min permitted levels. | Gas bottle explosion | All explosions are now being recorded to log the extent of the challenge. LondonEnergy is also investigating the potential of implementing ‘Storing and depressurising nominally empty nitrous oxide canisters: RPS 289’, which will support the correct disposal of gas canisters.
2023-10-26 | YP3033BE_EP_2023_AE028 | following a significant explosion within boiler 5, a high drum level alarm was triggered, forcing the boiler into emergency shutdown. This resulted in pro-longed elevated emissions at the A2 North stack as the boiler became off-line. The operations department conducted their standard shut-down checks and following cool-down of the boiler and on inspection, there was some integrity damage to the quench bath from the explosion. Recording of the boiler 5 camera clearly indicates the explosion occurring at 17:07 pm. | Boiler explosion | All explosions are now being recorded to log the extent of the challenge. LondonEnergy is also investigating the potential of implementing ‘Storing and depressurising nominally empty nitrous oxide canisters: RPS 289’, which will support the correct disposal of gas canisters.
2023-12-02 | YP3033BE_EP_2023_AE029 | 1 x 30 minute TOC exceedance – Boiler 3 experienced some extremely volatile waste, which created several large spikes in TOC’s and three large CO spikes. TOC levels during the 30 minute period were elevated and reduced significantly once combustion became stabilised. Several adjustments were made to combustion in an attempt to reduce the elevated levels. We were however unable to recover to within permitted levels within the specified time frame. | Waste quality | Waste inspections are continuing on the tipping apron by the waste operations team and any non-conforming waste segregated.
2023-12-16 | YP3033BE_EP_2023_AE030 | Explosion within the boiler resulted in a sharp elevation for both TOC and CO emissions. Due to the nature of the emission, the 30-minute exceedance for TOC was exceeded. | Gas bottle explosion | All explosions are now being recorded to log the extent of the challenge. LondonEnergy is also investigating the potential of implementing ‘Storing and depressurising nominally empty nitrous oxide canisters: RPS 289’, which will support the correct disposal of gas canisters.

## 2024
Date | Description of Event | Reason | Measures taken to prevent reoccurrence
2024-01-07 | YP3033BE_EP_2024_AE001 - Short-term TOC breach caused by a gas bottle explosion. 27.0mg/Nm3-C | Gas bottle explosion | Track explosion activity to gather data on the extent of challenge. Encourage and support the collection and segregation of gas canisters at recycling centres. | Information taken directly from EAs annual performance report template for 2024. The EAs annual performance report was modified in 2023 for operators to include information associated with permit exceedances. Information provided in the annual performance report associated with exceedances are displayed.
2024-01-14 | YP3033BE_EP_2024_AE003 - Multiple TOC and CO breaches | Loss of boiler communication system | Faulty units repaired, critical spares also brought in. Procedure on response to loss of communication updated.
2024-01-25 | YP3033BE_EP_2024_AE005 Multiple TOC and CO breaches A2 Stack | ID fan trip as a result of electrical work elsewhere | TBT to be delivered to the E&I in relation to incident.
2024-02-08 | YP3033BE_EP_2024_AE006 - CO 95th%ile breach 200mg/Nm3-C | Power supply failure | Preventative maintenance undertaken to ensure power supply does not fail again.
2024-03-08 | YP3033BE_EP_2024_AE008 - CO Daily and 95th%ile breach A1 Stack. | Tube leak and explosions
2024-03-18 | YP3033BE_EP_2024_AE009 - 1 x Short term TOC A2 stack, 24.1 mg/Nm3-C | Gas burner tripped while bringing boiler offline | Upgrades to sequencer on boiler 4 holding burner
2024-04-21 | YP3033BE_EP_2024_AE010 - 1 x Short term TOC A2 stack, 20.9 mg/Nm3-C | Gas bottle explosion | Collaboration with ops team and NLWA to tackle challenge with non-conforming waste in municipal waste
2024-04-23 | YP3033BE_EP_2024_AE011 - Daily average A2 stack, 183.35 mg/Nm3-C | Carbamine dosing issue | Create a carbamine tank clean PPM. Standby carbamine will be used while main tank is cleaned. Modification to carbamine pipework to be completed.
2024-04-23 | YP3033BE_EP_2024_AE012 - 1 x Short term TOC A1 stack, 44 mg/Nm3-C | Gas bottle explosion | Data collection and analysis on explosions
2024-04-26 | YP3033BE_EP_2024_AE013 - CO Daily and 95th%ile | Feeder ram trip | More frequent inspections of the parts that failed.
2024-05-17 | YP3033BE_EP_2024_AE014 - TOC Short Term Exceedance A2 Stack 22.4mg/Nm3-C | Burner issues | Burner specialist brought in to identify causes
2024-06-10 | YP3033BE_EP_2024_AE015 - TOC Short Term Exceedance A1 Stack 20.1mg/Nm3-C | Gas bottle explosion | Ongoing data tracking and analysis into explosions to identify patterns in their occurrence to explore if there are any preventative options.
2024-06-16 | YP3033BE_EP_2024_AE016 - TOC Short Term Exceedance A2 Stack 20.8mg/Nm3-C | Gas bottle explosion
2024-06-23 | YP3033BE_EP_2024_AE017 - TOC Short Term Exceedance A2 Stack 24.9mg/Nm3-C | Gas bottle explosion
2024-06-25 | YP3033BE_EP_2024_AE018 - TOC Short Term Exceedance A2 Stack 35.2mg/Nm3-C | Gas bottle explosion
2024-07-01 | YP3033BE_EP_2024_AE019 - TOC Short Term Exceedance A2 Stack 20.3mg/Nm3-C | Gas bottle explosion
2024-07-03 | YP3033BE_EP_2024_AE020 - TOC Short Term Exceedance A1 Stack 23.7mg/Nm3-C | Gas bottle explosion
14.07.2024 | YP3033BE_EP_2024_AE022 - TOC Short Term Exceedance A1 Stack 27mg/Nm3-C | Gas bottle explosion
25.07.2024 | YP3033BE_EP_2024_AE023 - TOC Short Term Exceedance A2 Stack 22.6mg/Nm3-C | Gas bottle explosion
10.08.2024 | YP3033BE_EP_2024_AE024 - TOC Short Term Exceedance A2 Stack 26.1mg/Nm3-C | Gas bottle explosion
2024-08-17 | YP3033BE_EP_2024_AE025 - Short term HCl and SO2 exceedance and daily HCl exceedance of 9.92mg/Nm3-C | Issue with lime delivery | Lime delivery contract was amended to ensure pick-up and of lime and delivery are the same day. KPIs are also now recorded and discussed with delivery partner in contract meetings.
2024-08-17 | YP3033BE_EP_2024_AE026 - CO Daily and 95th%ile, 68.77mg/Nm3-C and 281mg/Nm3-C respectively, A1 stack | PA fan failure | Average was brought back down following PA equipment failure. but explosions later in the day caused exceedance.
2024-08-17 | YP3033BE_EP_2024_AE027 - Two short term TOC 137.3mg/Nm3-C and 31.5mg/Nm3-C, A1 stack | Explosion | Ongoing data tracking and analysis into explosions to identify patterns in their occurrence to explore if there are any preventative options.
2024-08-23 | YP3033BE_EP_2024_AE028 - Short term TOC 26.4mg/Nm3-C, A1 stack | Gas bottle explosion
2024-08-27 | YP3033BE_EP_2024_AE029 - Short term TOC 27.6mg/Nm3-C, A1 stack | Gas bottle explosion
2024-08-28 | YP3033BE_EP_2024_AE030 - CO 95th%ile A1 Stack, 152.3mg/Nm3-C | Feeder ram and roller grate 1 issues | A 'slice' was installed into the feeder ram hydraulics to increase flow. In the longer term new proportional valves are to be installed on feeder ram.
2024-08-31 | YP3033BE_EP_2024_AE031 - Short term TOC, A2 Stack, 20.4mg/Nm3-C | Gas bottle explosion | Ongoing data tracking and analysis into explosions to identify patterns in their occurrence to explore if there are any preventative options.
2024-09-11 | YP3033BE_EP_2024_AE032 - Two short term TOC 22mg/Nm3-C and 24mg/Nm3-C, A1 stack | Gas bottle explosions
2024-09-14 | YP3033BE_EP_2024_AE033 - Short term TOC, A1 Stack, 20.6mg/Nm3-C | Gas bottle explosions
2024-09-17 | YP3033BE_EP_2024_AE034 - Short term TOC, A1 Stack, 41.1mg/Nm3-C | Gas bottle explosions
2024-09-20 | YP3033BE_EP_2024_AE035 - Short term TOC, A1 Stack, 49.3mg/Nm3-C | Gas bottle explosions
2024-09-21 | YP3033BE_EP_2024_AE036 - Short term TOC, A1 Stack, 22.3mg/Nm3-C | Gas bottle explosions
2024-10-01 | YP3033BE_EP_2024_AE037 - Short term dust breach A1 Stack 32.5mg/Nm3-C | FGT pre-heat dampener open | Added an interlock to prevent pre-heat dampener opening when the FGT is in an online state.
2024-10-10 | YP3033BE_EP_2024_AE039 - Periodic monitoring Dioxins breach, A2 Stack, 0.1816ng/m3 | PAC dosing issue | Review low alarm sequence for PAC dosing system, consistently across all streams, and carry out calibration check on dosing flow meters. Also lessons learnt are carried out with operations team.
2024-11-25 | YP3033BE_EP_2024_AE044 - Short term TOC, A2 Stack, 28.5mg/Nm3-C | Gas bottle explosions | Ongoing data tracking and analysis into explosions to identify patterns in their occurrence to explore if there are any preventative options.
2024-11-29 | YP3033BE_EP_2024_AE045 - NH3 daily average exceedance, 15.88 mg/Nm3-C | Dosing concentrated carbamine following plant trip | Review possibility for integrating engineering controls to stop dosing carbamine should NH3 go too high.
2024-12-10 | YP3033BE_EP_2024_AE049 - Short term TOC, A1 Stack, 27mg/Nm3-C | Gas bottle explosion | Ongoing data tracking and analysis into explosions to identify patterns in their occurrence to explore if there are any preventative options.

## 2025
Date | Description of Event | Pollutant | Exceedance Type | Best estimate of the quantity or the rate of emission | Measures taken, or intended to be taken, to prevent a recurrence of the incident.
2025-01-09 | After various explosions on the boilers the plant technicians changed around the air in the boiler to assist with better combustion to combat the high CO and to try stop any explosions, we also changed which bunker we were getting waste from which helped a great deal and settled the emissions down. It is anticipated that the challenges with CO were as a result of shredded waste received from the transfer station, which will be investigated. | CO | 95th %ile | 152 mg/Nm3 | Following internal investigation with the operations department, the following preventive actions have been identified: Look at potential of sending a portion of problematic shredded waste up to the bunker during daytime to support facilitate mixing prior to loading into hopper. 2-weekly sprint meeting to be introduced to review shredded waste challenges on the Energy Centre and review on-going performance Since carrying out minor alterations and collaboration between both the energy center and the RFPF waste operations team, we have seen an improvement and haven’t had any exceedances since the 12th of February.
2025-01-20 | It was observed when feeding boiler 1 and 2 there was a sharp change in waste composition, which in effect resulted in elevated acidic emissions being recorded at the stack. Lime dosing continued in Flue Gas Treatment 2, but was not effective in reducing the emissions to below the 30-minute ELV. Investigation into the waste is to be completed. | SO2 | Short-Term (30-minute) | 249.2 mg/Nm3 | Following internal investigation with the operations department, the following preventive actions have been identified: Look at potential of sending a portion of problematic shredded waste up to the bunker during daytime to support facilitate mixing prior to loading into hopper. 2-weekly sprint meeting to be introduced to review shredded waste challenges on the Energy Centre and review on-going performance
2025-01-27 | The 3 CO spikes at 4:39, 4:49 & 5:39 were due to extremely volatile waste taking off in Boilers 4 & 5 which were dealt with in the normal operational means by managing the combustion parameters and reducing the firing rate. | CO | 95th %ile | 151.4 mg/Nm3
2025-02-12 | It was observed when feeding boiler 1 and 2 there was a sharp change in waste composition, which in effect resulted in elevated acidic emissions being recorded at the stack. Lime dosing continued in Flue Gas Treatment 2, but was not effective in reducing the emissions to below the 30-minute ELV. Investigation into the waste is to be completed. | SO2 | Short-Term (30-minute) | 244.9 & 333.3 mg/Nm3 | Following internal investigation with the operations department, the following preventive actions have been identified: Look at potential of sending a portion of problematic shredded waste up to the bunker during daytime to support facilitate mixing prior to loading into hopper.
05/01/2025, 10/01/2025, 09/02/2025, 28/03/2025, 02/04/2025, 09/04/2025, 11/04/2025, 12/04/2025, 14/04/2025, 29/04/2025, 03/05/2025, | Multiple TOC Exceedances due to gas bottle explosions. Gas bottles entering the municipal waste stream causing a sharp elevation in TOC emissions, resulting in a 30-minute Exceedance. | TOC | Short-Term (30-minute) | (11 instances) marginally over the 30-minute Emission Limit Value | The waste inspection program is to be evaluated and appropriate recommendations / improvements are to be developed as part of the review. Due to the number of short-Term exceedances of TOC observed at the site, a permit variation to change the short-term Emission Limit Value to a 97th Annual %ile has been submitted.
2025-03-19 | Periodic monitoring report received on 17th April noted an exceedance of Dioxins and Furans on the A2 stack. This exceedance was due to a failure of the PAC dosing system on FGT3 which overlapped with the periodic monitoring. A blockage was identified on the PAC system following a review of the PAC operational performance. | Dioxin and Furans | Periodic Testing | 0.54 ng/m3 | Following a thorough incident review with the operations department, Several engineering controls have been put in place to prevent re-occurance and indicate a healthy state for the system: - Implement MOC to replicate lime system – if screw feeders are not running – flow indicator to revert to 0. - Conduct a review of the past dioxin monitoring and collate PAC dosing conditions to fully understand the minimum pinch point of operation to remain in compliance. - Review FGT Operator handbook to ensure specifics of PAC operations is included in sufficient detail to aid training. Explore if PAC dosing be added to DAHS to show healthy state of pollutant control. - Organise periodic monitoring company to come and do monthly re-testing across 3-months of Dioxins and Furans as per the monitoring protocol. - Conduct HIA assessment for incident.
2025-05-08 | Several explosions on boiler 5 was the primary reason for the exceedances. The plant technicians adjusted air in the boiler to assist with better combustion and reduce the high CO. The waste being fed at the time was from the bottom of bunker 3. The crane drivers were asked to stop feeding boiler 5 from bunker 3, as the other boilers seemed to be controlling CO a lot better. Boiler 5 was also put on gas to help control combustion. | CO | 95th %ile | 164.4 mg/Nm3 | Unlike originally thought, the CO issues were actually likely to be due to the beginning of a tube leak on the boiler causing combustion issues. Repairs were conducted to the boiler when taken off-line.
2025-05-09 | Boiler 5 experienced issues with TOC spikes and control. Whilst boiler adjustments were made to combustion control parameters, it became evident that transmitters for air flow were suspected to be at fault, therefore we stopped feeding waste to Boiler 5 at 06:00. In addition, despite no obvious signs of boiler overfeeding, a tube leak was later found on the front wall nose, which would have been spraying boiler water directly over the waste bed, effecting temperature and moisture content in the waste. | TOC | Short-Term (30-minute) | 63.5 , 218.9, 34.5 mg/Nm3
2025-04-14 | Report received for Dioxin and Furans monitoring conducted on the 15th April. The aim of the visit was to capture the dioxin profile during Boiler 5 start-up as required by WI BREF. Boiler 5 start-up was delayed, which resulted in the monitoring campaign missing the opportunity to capture start-up data, however monitoring was undertaken nonetheless. The resultant data did indicate elevated dioxin concentration, which is to be investigated. | Dioxin and Furans | Periodic Testing | 0.12 mg/Nm3 | Additional monitoring is to be arranged during the next Flue Gas Treatment outage (1 FGT operation on a stack) to confirm the increased dosing of PAC is sufficient to maintain compliance during similar outage periods. This was completed and results were within compliance with the environment permit.
2025-05-16 | The operations team identified an engineering fault on the Lime dosing system, specifically a fault with the butterfly valve. This resulted in poor lime delivery into the Flue gas, which unfortunately resulted in an exceedance on 2 x 30 minute averages: 06:59am – 65.7 mg/Nm3 and 07:29am – 82.1 mg/Nm3. | HCl | Daily Average | 12 mg/Nm3 (Daily Average) 65.7 & 82.1 mg/Nm3 (30-minute average) | Review the previous failure rate of theasset/valve to ensure this is an isolated event and not a systematic issue that requires a more frequent maintenance schedule.
2025-06-28 | Boiler 1 had an increase in CO and TOC spikes from 06:30. Various adjustments were made on combustion control parameters (Primary, Secondary air flow, Feeder Ram and Roller Grate speed). An attempt was made to feed waste from a different Bunker – This proved to make no difference so we stopped feeding Boiler 1, gate seal shut at 09:25 | CO | Daily Average | 81.28 mg/Nm3 | The cause of the exceedance has been very difficult to determine. At the time of the issue all combustion parameters were tweaked, different waste was fed and the boiler was put on gas. After the gate seal was shut as described in the part A notification, the boiler was brought offline to be inspected, suspecting there may be a tube leak. No issues were found that could’ve causing CO issues.
2025-07-13 | At approximately 17:40 yesterday a fire was detected by an infrared fire detector within the turbine itself. It is anticipated that the fire had been caused by oil dripping on to steam pipework situated below the Turbine itself. On the front end of the Turbines, there is a HP Bearing which has an oil seal (Inproseal) which often leak and therefore purpose built drip trays are installed to safely capture the oil and transfer it to a container. Personnel were accounted for and unharmed. | N/A | N/A | N/A | A thorough incident review was conducted.The actions identified were broken down into the following categories: - 1 Elimination action - 2 Substitution actions - 8 Engineering actions - 12 Administrative actions - 1 PPE action - 6 Environment Actions All actions are to be logged on the sites incident reporting and tracking system with appropriate timelines for completion.
2025-08-07 | Waste was being run off the grate and external work had been started for the repair of the riddling conveyor. Air was reduced and burners were initiated to control emissions, however as the quench bath water level had to be drained to a lower level, a large amount of cold air was being drawn into the boiler. The high O2 percentage entering the boiler led to difficulties with controlling the combustion profile and thus caused CO emissions. | CO | 95th %ile | 184.4 mg/Nm3 | A re-brief of the procedure will be given to the operations team including shift managers via the form of a toolbox talk to remind the team of the process.